## USA Calculator
Xpress Resin US Calculator
Instructions: Input data into the yellow boxes
Pipe Diameter (inches) | Minmum recommended # of coats (avg thickness = 1mm per coat) | # of Coats to be Applied | Pipe Length (Feet) | Strokes / Feet | Total number of strokes | Resin Comsumption (US Gallons) | Number of Buckets (Per Component)
1.25" | 2 |  |  | 0.011371 | 0 | 0 | 0
1.5" | 2 |  |  | 0.015279 | 0 | 0 | 0
2" | 2 |  |  | 0.019186 | 0 | 0 | 0
3" | 2 |  |  | 0.028956 | 0 | 0 | 0
4" | 3 to 4 |  |  | 0.038725 | 0 | 0 | 0
5" | 3 to 4 |  |  | 0.048494 | 0 | 0 | 0
6" | 4 to 5 |  |  | 0.058263 | 0 | 0 | 0
8" | 5 to 6 |  |  | 0.077801 | 0 | 0 | 0
9" | 6 to 7 |  |  | 0.08757 | 0 | 0 | 0
10" | 6 to 7 |  |  | 0.097339 | 0 | 0 | 0
12" | 8 to 9 |  |  | 0.11688 | 0 | 0 | 0

## Scale (US)
[7 empty] | 1 |  | litre = | 0.264 | US gallon
Xpress Coating Scale (USA)
Scale is the maximum distance one full stroke of the Xpress Pump will cover.
Scale |  |  | Pipe Diameter (Inches)
% | Litres | US Gallons | 1 1/4" | 1 1/2" | 2" | 3" | 4" | 5" | 6" | 8" | 9" | 10" | 12"
0% | 2.2 | 0.5808 | 27 | 20 | 16 | 10 | 8 | 7 | 6 | 4 | 3.5 | 3 | 2.6
0% | 2.2 | 0.5808 | 88.5827 | 65.6168 | 52.4934 | 32.8084 | 26.2467 | 22.9659 | 19.685 | 13.1234 | 11.4829 | 9.8425 | 8.5302
5% | 2.09 | 0.55176 | 84.1535 | 62.336 | 49.8688 | 31.168 | 24.9344 | 21.8176 | 18.7008 | 12.4672 | 10.9088 | 9.3504 | 8.1037
10% | 1.98 | 0.52272 | 79.7244 | 59.0551 | 47.2441 | 29.5276 | 23.622 | 20.6693 | 17.7165 | 11.811 | 10.3346 | 8.8583 | 7.6772
15% | 1.87 | 0.49368 | 75.2953 | 55.7743 | 44.6194 | 27.8871 | 22.3097 | 19.521 | 16.7323 | 11.1549 | 9.7605 | 8.3661 | 7.2507
20% | 1.76 | 0.46464 | 70.8661 | 52.4934 | 41.9948 | 26.2467 | 20.9974 | 18.3727 | 15.748 | 10.4987 | 9.1864 | 7.874 | 6.8241
25% | 1.65 | 0.4356 | 66.437 | 49.2126 | 39.3701 | 24.6063 | 19.685 | 17.2244 | 14.7638 | 9.8425 | 8.6122 | 7.3819 | 6.3976
30% | 1.54 | 0.40656 | 62.0079 | 45.9318 | 36.7454 | 22.9659 | 18.3727 | 16.0761 | 13.7795 | 9.1864 | 8.0381 | 6.8898 | 5.9711
35% | 1.43 | 0.37752 | 57.5787 | 42.6509 | 34.1207 | 21.3255 | 17.0604 | 14.9278 | 12.7953 | 8.5302 | 7.4639 | 6.3976 | 5.5446
40% | 1.32 | 0.34848 | 53.1496 | 39.3701 | 31.4961 | 19.685 | 15.748 | 13.7795 | 11.811 | 7.874 | 6.8898 | 5.9055 | 5.1181
45% | 1.21 | 0.31944 | 48.7205 | 36.0892 | 28.8714 | 18.0446 | 14.4357 | 12.6312 | 10.8268 | 7.2178 | 6.3156 | 5.4134 | 4.6916
50% | 1.1 | 0.2904 | 44.2913 | 32.8084 | 26.2467 | 16.4042 | 13.1234 | 11.4829 | 9.8425 | 6.5617 | 5.7415 | 4.9213 | 4.2651
55% | 0.99 | 0.26136 | 39.8622 | 29.5276 | 23.622 | 14.7638 | 11.811 | 10.3346 | 8.8583 | 5.9055 | 5.1673 | 4.4291 | 3.8386
60% | 0.88 | 0.23232 | 35.4331 | 26.2467 | 20.9974 | 13.1234 | 10.4987 | 9.1864 | 7.874 | 5.2493 | 4.5932 | 3.937 | 3.4121
65% | 0.77 | 0.20328 | 31.0039 | 22.9659 | 18.3727 | 11.4829 | 9.1864 | 8.0381 | 6.8898 | 4.5932 | 4.019 | 3.4449 | 2.9856
70% | 0.66 | 0.17424 | 26.5748 | 19.685 | 15.748 | 9.8425 | 7.874 | 6.8898 | 5.9055 | 3.937 | 3.4449 | 2.9528 | 2.5591
75% | 0.55 | 0.1452 | 22.1457 | 16.4042 | 13.1234 | 8.2021 | 6.5617 | 5.7415 | 4.9213 | 3.2808 | 2.8707 | 2.4606 | 2.1325
80% | 0.44 | 0.11616 | 17.7165 | 13.1234 | 10.4987 | 6.5617 | 5.2493 | 4.5932 | 3.937 | 2.6247 | 2.2966 | 1.9685 | 1.706
85% | 0.33 | 0.08712 | 13.2874 | 9.8425 | 7.874 | 4.9213 | 3.937 | 3.4449 | 2.9528 | 1.9685 | 1.7224 | 1.4764 | 1.2795
90% | 0.22 | 0.05808 | 8.8583 | 6.5617 | 5.2493 | 3.2808 | 2.6247 | 2.2966 | 1.9685 | 1.3123 | 1.1483 | 0.98425 | 0.85302
95% | 0.11 | 0.02904 | 4.4291 | 3.2808 | 2.6247 | 1.6404 | 1.3123 | 1.1483 | 0.98425 | 0.65617 | 0.57415 | 0.49213 | 0.42651
100% | 0 | 0 | -3.5527e-14 | 0 | 0 | 0 | 0 | -1.0658e-14 | 0 | 0 | -5.3291e-15 | 0 | 1.5543e-15

## Metric Calculator
Xpress Resin Metric Calculator
Instructions: Input data into the yellow boxes
Pipe Diameter (mm) | Minmum recommended # of coats (avg thickness = 1mm per coat) | # of Coats to be Applied | Pipe Length (metres) | Strokes / metre | Total number of strokes | Resin Comsumption (Litres) | Number of Buckets (Per Component)
32 | 1 |  |  | 0.037298 | 0 | 0 | 0
40 | 1 |  |  | 0.050115 | 0 | 0 | 0
50 | 2 |  |  | 0.062932 | 0 | 0 | 0
75 | 2 |  |  | 0.094974 | 0 | 0 | 0
100 | 3 to 4 |  |  | 0.12702 | 0 | 0 | 0
125 | 3 to 4 |  |  | 0.15906 | 0 | 0 | 0
150 | 4 to 5 |  |  | 0.1911 | 0 | 0 | 0
200 | 5 to 6 |  |  | 0.25519 | 0 | 0 | 0
225 | 6 to 7 |  |  | 0.28723 | 0 | 0 | 0
250 | 6 to 7 |  |  | 0.31927 | 0 | 0 | 0
300 | 8 to 9 |  |  | 0.38336 | 0 | 0 | 0

## Scale (Metric)
[7 empty] | 1 |  | litre = | 0.264 | US gallon
Xpress Coating Scale (Metric)
Scale is the maximum distance one full stroke of the Xpress Pump will cover.
Scale |  |  | Pipe Diameter (MM)
% | Litres | US Gallons | 32 | 40 | 50 | 70 | 100 | 125 | 150 | 200 | 225 | 250 | 300
0% | 2.2 | 0.5808 | 27 | 20 | 16 | 10 | 8 | 7 | 6 | 4 | 3.5 | 3 | 2.6
5% | 2.09 | 0.55176 | 25.65 | 19 | 15.2 | 9.5 | 7.6 | 6.65 | 5.7 | 3.8 | 3.325 | 2.85 | 2.47
10% | 1.98 | 0.52272 | 24.3 | 18 | 14.4 | 9 | 7.2 | 6.3 | 5.4 | 3.6 | 3.15 | 2.7 | 2.34
15% | 1.87 | 0.49368 | 22.95 | 17 | 13.6 | 8.5 | 6.8 | 5.95 | 5.1 | 3.4 | 2.975 | 2.55 | 2.21
20% | 1.76 | 0.46464 | 21.6 | 16 | 12.8 | 8 | 6.4 | 5.6 | 4.8 | 3.2 | 2.8 | 2.4 | 2.08
25% | 1.65 | 0.4356 | 20.25 | 15 | 12 | 7.5 | 6 | 5.25 | 4.5 | 3 | 2.625 | 2.25 | 1.95
30% | 1.54 | 0.40656 | 18.9 | 14 | 11.2 | 7 | 5.6 | 4.9 | 4.2 | 2.8 | 2.45 | 2.1 | 1.82
35% | 1.43 | 0.37752 | 17.55 | 13 | 10.4 | 6.5 | 5.2 | 4.55 | 3.9 | 2.6 | 2.275 | 1.95 | 1.69
40% | 1.32 | 0.34848 | 16.2 | 12 | 9.6 | 6 | 4.8 | 4.2 | 3.6 | 2.4 | 2.1 | 1.8 | 1.56
45% | 1.21 | 0.31944 | 14.85 | 11 | 8.8 | 5.5 | 4.4 | 3.85 | 3.3 | 2.2 | 1.925 | 1.65 | 1.43
50% | 1.1 | 0.2904 | 13.5 | 10 | 8 | 5 | 4 | 3.5 | 3 | 2 | 1.75 | 1.5 | 1.3
55% | 0.99 | 0.26136 | 12.15 | 9 | 7.2 | 4.5 | 3.6 | 3.15 | 2.7 | 1.8 | 1.575 | 1.35 | 1.17
60% | 0.88 | 0.23232 | 10.8 | 8 | 6.4 | 4 | 3.2 | 2.8 | 2.4 | 1.6 | 1.4 | 1.2 | 1.04
65% | 0.77 | 0.20328 | 9.45 | 7 | 5.6 | 3.5 | 2.8 | 2.45 | 2.1 | 1.4 | 1.225 | 1.05 | 0.91
70% | 0.66 | 0.17424 | 8.1 | 6 | 4.8 | 3 | 2.4 | 2.1 | 1.8 | 1.2 | 1.05 | 0.9 | 0.78
75% | 0.55 | 0.1452 | 6.75 | 5 | 4 | 2.5 | 2 | 1.75 | 1.5 | 1 | 0.875 | 0.75 | 0.65
80% | 0.44 | 0.11616 | 5.4 | 4 | 3.2 | 2 | 1.6 | 1.4 | 1.2 | 0.8 | 0.7 | 0.6 | 0.52
85% | 0.33 | 0.08712 | 4.05 | 3 | 2.4 | 1.5 | 1.2 | 1.05 | 0.9 | 0.6 | 0.525 | 0.45 | 0.39
90% | 0.22 | 0.05808 | 2.7 | 2 | 1.6 | 1 | 0.8 | 0.7 | 0.6 | 0.4 | 0.35 | 0.3 | 0.26
95% | 0.11 | 0.02904 | 1.35 | 1 | 0.8 | 0.5 | 0.4 | 0.35 | 0.3 | 0.2 | 0.175 | 0.15 | 0.13
100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8874e-15 | 0 | 0 | 0 | 0 | 0

## Design (hidden)
Recommended number of coats
Pipe Diameter | DC1000E | Xpress V1 | Xpress V2
DN 32 (1 1/4") | 2 | 2 | 2
DN 40 (1 1/2") | 2 | 2 | 2
DN 50 (2") | 2 | 2 | 2
DN 70 (3") | 3 to 4 | 2 to 3 | 2 to 3
DN 100 (4") | 3 to 4 | 3 to 4 | 3 to 4
DN 150 (6") | 4 to 5 | 4 to 5 | 4 to 5
DN 200 (8") | 5 to 6 | 4 to 5 | 5 to 6
DN 225 (9") | 6 to 7 | 5 to 6 | 6 to 7
DN 300 (12") | 8 to 9 | 6 to 7 | 8 to 9
Note:
1. A minumum of 4 coats need to be applied in the pipe is going to be cleaned using High Pressure Water Jetting
2. Maximum Water Jetting Pressure is 2600 PSI or 180 Bar
3. A minimum of 3 coats need for abrasion resistance.

## Olav Workings (hidden)
|  |  |  | Cylinder diam: | 60
|  |  |  | Piston Stroke: | 390 | 0.58 | US Gallons |  | USA | 5.8 | 10.98
| Layer thickness: | 0.9 |  | 1 pumpstroke: | 2206000 | 2.2 | Litres |  | Metric | 22
Layers | 1 | 2 | 3
30 | 82278.3116 | 159467.2431 | 231566.7945
40 | 110552.6455 | 216015.9109 | 316389.7961
50 | 138826.9794 | 272564.5786 | 401212.7978 |  | A=π(R^2-r^2) | 153.938 | mm²
75 | 209512.8141 | 413936.248 | 613270.3019 |  | V=π(R^2-r^2)*h | 153938.04 | mm³ | 1 meter 1mm layer
100 | 280198.6488 | 555307.9174 | 825327.806
125 | 350884.4835 | 696679.5869 | 1037385.3101
150 | 421570.3182 | 838051.2563 | 1249442.8143 |  |  | A=πr^2
200 | 562941.9876 | 1120794.5951 | 1673557.8225 |  | Outer diameter | 1963.4954 | mm²
225 | 633627.8223 | 1262166.2645 | 1885615.3266 |  | Inner diameter | 1809.5574 | mm²
250 | 704313.657 | 1403537.9339 | 2097672.8307 |  | Ring surface area | 153.938 | mm²
300 | 845685.3264 | 1686281.2727 | 2521787.839 |  | 1m volume | 153938.04 | mm³
Strokes to achieve a 1 meter 3mm surface in pipesizes: |  |  |  | Strokes to achieve a 1 meter and 1 coat in pipesizes:
32 | 0.10497 | 10.5% |  | 32 | 0.037298
40 | 0.14342 | 14.34% |  | 40 | 0.050115
50 | 0.18187 | 18.19% |  | 50 | 0.062932
75 | 0.278 | 27.8% |  | 75 | 0.094974
100 | 0.37413 | 37.41% |  | 100 | 0.12702
125 | 0.47026 | 47.03% |  | 125 | 0.15906
150 | 0.56638 | 56.64% |  | 150 | 0.1911
200 | 0.75864 | 75.86% |  | 200 | 0.25519
225 | 0.85477 | 85.48% |  | 225 | 0.28723
250 | 0.95089 | 95.09% |  | 250 | 0.31927
300 | 1.1431 | 114.3% |  | 300 | 0.38336
Meters that can be coated with 1 stroke 3mm thickness in pipe sizes |  |  |  | Meters that can be coated with 1 stroke 0,9mm thickness in pipe sizes
32 | 9.5264 |  |  | 32 | 26.8114
40 | 6.9724 |  |  | 40 | 19.9543
50 | 5.4983 |  |  | 50 | 15.8903
75 | 3.5971 |  |  | 75 | 10.5292
100 | 2.6729 |  |  | 100 | 7.873
125 | 2.1265 |  |  | 125 | 6.287
150 | 1.7656 |  |  | 150 | 5.2328
200 | 1.3181 |  |  | 200 | 3.9187
225 | 1.1699 |  |  | 225 | 3.4815
250 | 1.0516 |  |  | 250 | 3.1321
300 | 0.87478 |  |  | 300 | 2.6085
Note on C7: Olav Törnroos: Volume of 1 meter, 1mm layer V=π(R^2-r^2)*h
Note on C8: Olav Törnroos: Volume of 1 meter, 1mm layer V=π(R^2-r^2)*h
Note on C9: Olav Törnroos: Volume of 1 meter, 1mm layer V=π(R^2-r^2)*h